## Coordination
Coordination Preparation Check Sheet
| Done By? |  | Date:
Item | Description | Person Responsible | Deadline | Status
1 | Project manager assigned
2 | Networking team lead identified
3 | Transportation team lead identified
4 | Server area team lead identified
5 | Server team lead identified
6 | Customer communication lead identified.
7 | Catered food lead identified (Pizza, Veggie, Kosher, Halal, etc.)
8 | Post mortem team created to analyze any failures in the process.
9 | Gofer identified
10 | Disaster recovery team lead identified
11 | All members of the relocation team will have functioning mobile phones on the day or the migration.
12 | Conference call bride arranged
13 | Best time and date for relocation identified
14 | Team aware of method to be used to identify malfunctioning equipment.
15 | Short list of scenarios during which the relocation will have to be rolled back has been created.
16 | Point of no return identified.
17 | Minimum list of functional servers for successful migration created.
18 | Sequence list of which equipment will be moved, and when, created.
19 | Roll back plan created that includes the sequence in which equipment will be returned.
20 | Server list / inventory spreadsheet has been created and distributed to all teams.
21 | Application audit performed for all servers to account for interdependencies with other applications.
22 | Procedures documentation completed for each server / network device
23 | Equipment that will have to be leased or purchased to facilitate the relocation has been obtained

## Communication
Customer Communication Check Sheet
| Done By? |  | Date:
Item | Description | Person Responsible | Deadline | Status
1 | Single message of varying degrees of detail created for each customer group.
2 | Internal customers alerted of plan
3 | External customers alerted of plan
4 | Draft notifications to be used in the event of failure and success created.
5 | Short list of customers to be kept updated by phone created.
6 | Post mortem template identified

## Data Center
Server Area Preparation Check Sheet
| Done By? |  | Date:
Item | Description | Person Responsible | Deadline | Status
1 | Racks and cabinets installed in new location.
2 | Correct power supplied to each rack and cabinet
3 | Each PDU in the server area can handle the failure of the other redundant one supplying the area.
4 | Adequate cooling provided for expected server heat load.
5 | Power outlets are labeled to indicate the PDU that supplies them.
6 | Verify that you have power cables in sufficient quantities and adequate lengths.
7 | Power cables are labeled at both ends.
8 | Power supplied is of the correct voltage using the desired connectors.
9 | Servers in racks and cabinets won't overload the power circuits that supply them.
10 | Diagrams created to show the server layout in the racks or cabinets.
11 | Shelving and rack kits for servers pre installed in cabinets and racks.
12 | KVM (Keyboard, Video Monitor, Mouse) switches preinstalled.
13 | Rack mounted keyboards and monitors installed in cabinets or racks.
14 | Racks and cabinets clearly indicate the server orientation to create hot and cold aisles.
15 | Keys given to all persons who require access to the server area.
16 | Staff doing the server "Rack and Stack" work have adequate tools especially electric screwdrivers.
17 | Data circuits for internet connectivity have been run to the racks to be used by the networking equipment.
18 | Monitors on carts available for troubleshooting servers that need to be removed from racks.
21 | Patch panels installed correctly
22 | Patch panels have the correct connectors.
23 | Cable lengths through the patch panels are under 100m in length.
26 | Aisles between racks wide enough to allow people to easily mount and dismount servers in them.
27 | Server area has 24/7 video surveillance
28 | Server area has biometric or some other form of keyless entry system access system.
29 | Copper data cables, fiber data cables and power cables run in separate conduits or trays.
30 | Data cables not hanging in the air or pulled taught.
31 | Patch panel cable bundles run to the sides of racks and cabinets so as not to impede airflow.
32 | Adjacent server cabinets do not have their walls removed.
33 | Few air flow obstacles under the raised floor area.
35 | Raised floor under the cooling zone of each CRAC unit is sealed to force air through desired cabinets.
36 | Perforated floor tiles only used in cold aisles.

## Network
Network Preparation Check Sheet
| Done By? |  | Date:
Item | Description | Person Responsible | Deadline | Status
1 | Network equipment with dual power supplies are plugged into electrical circuits from each PDU.
2 | Groups of servers with similar function (eg. DB servers) are connected to redundant switches in a 50/50 fashion.
3 | Each server is labeled on the front and back.
4 | Data circuits to be used by the network gear have been tested.
5 | Sample configurations have been created for all networking devices with the new network addresses to be used at the new location.
6 | The standby devices in redundant pairs of networking equipment at the old location have been shutdown, shipped to the new location and preconfigured.
7 | Complete network diagrams of the new location have been created.
8 | Test VPNs to remote offices have been created.
9 | Network devices are labeled in the front and back.
10 | All network cables labeled at both ends.
12 | Procedures documentation completed for each server / network device
13 | Data circuit capacity requirements identified for both production Web access and possible data replication between data centers.

## Server
Server Preparation Check Sheet
| Done By? |  | Date:
Item | Description | Person Responsible | Deadline | Status
1 | Servers with dual power supplies are plugged into electrical circuits from each PDU.
2 | Groups of servers with similar function (eg. DB servers) with single power supplies are connected to redundant PDUs in a 50/50 fashion.
3 | All server power cords labeled at both ends.
4 | Each server's "netstat -an" output has been recorded.
5 | Each server's "netstat -nr" output has been recorded with the expected output at the remote location prepared.
6 | Server data backed up.
7 | Practice data backups and restorations done for key servers and applications.
8 | All RAID BIOS settings record ed.available (replication scenario)
9 | Spare servers identified as possible sources of spare parts or as "hot standby" devices.
10 | Sequence of servers to be moved identified.
11 | Sequence of how the servers will be returned moved in the event of a roll back identified.
12 | Testing short list created for each server.
13 | Applications vetted to make sure they refer only to DNS names not IP addresses.
14 | Minimum list of servers for correct site functionality created.
15 | Special operating procedures for key servers created. (eg. Documentation of the sequence in which servers should be booted or applications started)
16 | Snapshots of the actively running services or applications for each server has been created.
17 | Procedures documentation completed for each server / network device
18 | Amount of data to be backed up per server has been determined.
19 | Equivalent amount of production data storage

## DNS
DNS Preparation Check Sheet
| Done By? |  | Date:
Item | Description | Person Responsible | Deadline | Status
1 | TTL on old DNS zone files set to 5 minutes and propagated to the Internet.
2 | New DNS zone files created with new IP addresses. (TTLs should remain at 5 minutes)
3 | Testing of application using new DNS entries in the test server's hosts file completed.
4 | Testing of website using new DNS entries in the web browser client PC's hosts file completed.

## Transportaion
Transportation Preparation Check Sheet
| Done By? |  | Date:
Item | Description | Person Responsible | Deadline | Status
1 | Moving truck rented / Professional movers hired
2 | Mover has adequate insurance coverage
3 | Adequate method for stacking and securing servers in the truck found.
4 | Equipment insurance up to date.
5 | Dollies and carts available at both locations for moving the servers across the floor.
6 | Boxes purchased or rented for moving equipment and miscellaneous items.
7 | Special packaging for the more delicate items.
8 | Items under maintenance contract prepared for transportation by the equipment vendor, not internally.

## During Relocation
During Relocation Check Sheet
| Done By? |  | Date:
Item | Description | Person Responsible | Deadline | Status
1 | Notifications sent to all customers that the activity is about to
2 | DNS using the new zone files has been propagated to the Internet.
3 | Emergency conference call bridge has been created for communication with team.

## Post Relocation
Post Relocation Check Sheet
| Done By? |  | Date:
Item | Description | Person Responsible | Deadline | Status
1 | All power cables labeled at both ends
2 | All network cables labeled at both ends
3 | Moving truck, dollies, carts, boxes and other transportation related items returned.
4 | New diagrams and other documentation created for adequate description of the new server environment.
5 | Error logging and monitoring occurring correctly.
6 | Contracts related to old facility terminated or re-negotiated for the new facility.
7 | All equipment at the new location has been restored to fully redundant operation.
8 | Redundancy testing of new server environment completed.
9 | Testing of data throughput rates at new location completed.
10 | Customers and partners can get adequate access to the servers at the new location.
11 | Test data backups of servers successful.
12 | DNS TTLs on new zone files have been reverted to a couple days.
13 | Security audits planned and executed.
14 | Blanking panels inserted between servers
15 | Server cable bundles run to the sides of racks and cabinets so as not to impede airflow.
16 | Ambient air temperature within design of the CRAC unit
17 | Ambient air humidity within design of the CRAC unit
18 | Intake temperature at the front of servers in the rack is within specification.
19 | Exhaust temperature at the front of servers in the rack is within specification.